Section 10 14 43

Ecoglo Photoluminescent Egress Path Markings

This specification has been numbered, organized and formatted in accordance with the MasterFormat, Section Format and Page Format documents published jointly by Construction Specifications Institute (CSI). For convenience, all products are contained within Section 10 14 43 (Photoluminescent Egress Path Markings) but if desired may be edited/adapted to suit any other Section(s) of Work in accordance with project requirements.

It is offered as a guide to experienced and knowledgeable construction professionals who assume full responsibility for its interpretation and use. Square brackets [ ] containing text indicate an option to be considered/inserted by the specifier. Remove brackets and unused options before printing.

Section 10 14 43

Photoluminescent Egress Path Markings

Part 1 General

1.1 	Summary

A 	  Work Included: Furnishing and installation of complete
                        photoluminescent Egress Path Marking System.

1      Stair and Leading Edge Markings

2      Handrail Markings

3      Perimeter Demarcation and Door Frame Markings

4      Obstacle Markings

5      Stairway/Floor Identification Signs

6      Egress Signage

7      Door Hardware Markings

1.2 	Related Sections:

A 	  Division 01: Administrative, procedural, and temporary work
                        requirements

B 	  Section 26 5213 - Photoluminescent Exit Signs.

C 	  Section 05 5500 – Photoluminescent (Metal) Stair Treads and
                        Nosings.

1.3	Design Requirements

A  	  Photoluminescent Exit Path Marking System shall be a complete
                       system of low level egress markings in compliance with the
                       requirements of the local building code and fire code.

B  	  Photoluminescent step edge marking products shall provide step
                        edge colour contrast and slip resistance.

1         Photoluminescent material shall be recessed within powder
                                   coated aluminium (aluminum) ridges which provide slip
                                   resistance and protect the photoluminescent material.
		  2         Photoluminescent material utilized in step edge markings shall
                                   not have an abrasive texture that collects dirt and results in
                                   lower photoluminescent performance.
		  3         Step edge products shall include an integrally bonded silicon
                                   carbide abrasive non-slip component that provides colour
                                   contrast.
  		  4         Step edge products shall be aluminium (aluminum) based and
                                   manufactured using High Temperature Curing (HTC)
                                   technology.
                                   Flexible tape products and vinyl materials are not acceptable.

C    	 Photoluminescent egress markings shall be 1 inch (25 mm) wide, or
                       UL 1994 listed.

D       Stairway/Floor Identification Signage in high rise buildings requiring
             photoluminescent egress markings are required to be made of
             photoluminescent material and must meet the following
             requirements.

1 	Signs shall be a minimum size of 18” x 12 inches (460 mm x 310
                                 mm).
		  2 	Include the Identification of Stair
		  3 	Roof Access Yes/No 
		  4 	Floor Number 
		  5 	Optional: Braille Floor Number 
		  6 	Termination top/Bottom of stair 
		  7 	Story and direction of exit discharge

1.4 	References

A 	  [National Fire Protection Association (NFPA) 101 - Life Safety Code]

B 	  [2009 International Building Code / International Fire Code (IBC/IFC)
 		  section 1024]

[2012 International Building Code / International Fire Code (IBC/IFC)
 		  section 1024]

[2015 International Building Code / International Fire Code (IBC/IFC)
 		  section 1025]

[2018 International Building Code / International Fire Code (IBC/IFC)
 		  section 1025]

C 	  [New York City LL 141 Photoluminescent Exit Path Markings section
 		   1024]

D 	  Underwriters Laboratories, Inc. (UL) UL 1994 Standard for Safety,
		  Luminous Egress Path Marking Systems.

E 	  American Society for Testing & Materials (ASTM) ASTM E2072,
		  Standard Specification for Photoluminescent (Phosphorescent) Safety
 		  Markings and E2073 – Standard Test Method for Photopic Luminance
 		  of Photoluminescent (Phosphorescent) Markings.

1.5      Quality Assurance

A 	  Manufacturer Qualifications: to have minimum of 20 years experience
 		  with similar work.

B 	  Installer Qualifications: to be manufacturer trained/authorized installer.

1.6      Submittals

A 	  Submit the following [in accordance with Section 01 33 00 – Submittal
 	   	  Procedures]:

1 	Product Data: Manufacturer’s product data sheets for materials
 			used in system.

2 	Shop Drawings: Provide drawings showing details, dimensions,
 			extent of work, and other data necessary for the satisfactory
 			installation of the products stated herein for compliance
			with the local building code requirements.

3 	Samples: 12” size for review showing final colour. Label
 			samples with product codes and intended use.

4 	Manufacturer’s Instructions: Pre-printed material describing
 			installation of product, system or material, including special
 			notices.

5 	Test Reports: Submit independent test reports to verify
 			compliance with relevant standards as detailed in 2.2A(3) and
 			2.2A(4).

6 	Substitutions: Substitutions must be submitted and approved
 			prior to bid date. All requests shall include test results, product
 			descriptions, 	confirmation of piece design and engineering
 			calculations meeting design criteria.

Include the following for submission of sustainable design submittals.

B	Sustainable Design Submittals:

1 	Regional Materials: Certify manufacturing location.

2	Construction Waste Management Divert from Land Fill: 
			Certify if products are made with materials that are recyclable.

3	Recycled Content: Certify percent recycled content and
 			designate whether pre-consumer or post-consumer.

4	VOC content for installation adhesives.

1.7	Delivery, Storage and Handling

A 	  Handle and store Products in a manner to prevent damage,
 		  deterioration and soiling to Products, other building components,
 		  assemblies, other Products, the structure, the Site and surrounding
 		  property and in accordance with manufacturer’s instructions.

B	  Store products subject to damage from weather in weatherproof
 		  enclosures.

1.8 	Warranty

A  	  Provide manufacturer’s limited warranty. Warranty to cover defects in
 		  materials and workmanship.

1 	High Temperature Curing (HTC) Products: (5) years from the
 			date of Substantial Performance of the Work.

2 	30 Year Warranty on photoluminescent performance of HTC
 			products when positioned indoors.

Part 2 Products

2.1 	Manufacturers

A 	  Contract Documents are based on products by Ecoglo International
 		  Ltd. (www.ecoglo.com)

B 	  Substitutions: [Under provisions of Division 01.] Submit for
 		  consideration prior to bid closing.

2.2 	Materials

A 	  High Temperature Curing (HTC) Products:

1 	Extruded Aluminium (Aluminum) Nosings: 6060T5 extrusion
 			anodized to Class 1, .0007” (20 microns) thickness.

2 	Photoluminescent material: manufactured using HTC technology
 			- strontium aluminate-based photoluminescent pigment
 			embedded in thermoset polyester carriers that integrally bond
 			the active ingredients into powder coated aluminium (aluminum)
 			substrates following curing at 350°F (180°C).

3 	Materials shall be UL 1994 listed.

4	All HTC products to meet or exceed the performance criteria
 			specified in the following tests or standards. PC = Performance
 			Criteria

a. Slip Resistance

UL 410 Standard for Slip Resistance for Floor Surface
 			       Materials, PC – Pass, or alternatively,
			       AS/NZS 4586-2004, Slip Resistance Classification of New
 			       Pedestrian Surface Materials. PC – Dry slip resistance
			       classification F, wet slip resistance classification V, slip
			       resistance assessment group R12
			       AS 4586-2013 PC - Classification: P5

b. UV Resistance

ASTM G155-04 Cycle 1 1000hrs, Standard Practice for
 			       Operating Xenon Arc Light Apparatus for Exposure of
 			       Nonmetallic Materials. PC – Loss in luminance after
 			       exposure < 10%

c. Salt Spray Resistance

ASTM B117-97 1000hrs, Standard Practice for Operating
 			       Salt Spray (Fog) Apparatus. PC – Slight corrosion build up
 			       along scribes, no blistering or filiform growth along scribes.

d. Washability

ASTM D4828-94(2003), Standard Test Methods for
 			       Practical Washability of Organic Coatings. PC – crayon,
 			       pen, 3M soil: all rating 10, being complete removal of
 			       soilant.

e. Rate of Burning

ASTM D635-03, Standard Test Method for Rate of Burning
 			       and/or Extent and Time of Burning of Plastics in a
 			       Horizontal Position. PC – Time of burn 0 seconds, does not
 			       burn.

f.  Surface Flammability

ASTM E162-02, Standard Test Method for Surface
 			       Flammability of Materials Using a Radiant Heat Energy
 			       Source. PC – Flame spread index 7.6, ignites with difficulty.

g. Toxicity

Bombardier Toxic Gas Generation Test SMP800-C.

PC – Pass.

h. Radioactivity

ASTM D3648-2004, Standard Practices for the
   	 Measurement of Radioactivity. PC – Pass.

i.  Luminance

UL 1994 Standard for Luminous Egress Path Marking
 			      Systems. PC – Pass.

j.  High Temperature Curing

Independently tested by placing 3 samples in an oven at
 			      180°C for 20 minutes and then examining the samples after
 			      removing from the oven. PC – the samples shall have no
 			      shrinkage, delamination, distortion, or yellowing.

5	Anti-slip surface: manufactured using HTC technology – silicon
 			carbide integrally bonded into powder-coated aluminium
 			(aluminum) substrates following curing at 350°F (180°C).

2.3 	Components

A   	  Step Edge Markings

1 	Step Edge Product Code: [E14-075]

Description: [64mm wide strip incorporating 10mm
 			photoluminescent strip and 50mm black anti-slip strip. Available
 			in lengths from 800mm to 1500mm in 100mm increments, or in
 			full lengths of 2450mm or 3060mm.]

SPEC NOTE: The listed data included in table below provide product codes and descriptions. Anti-slip in all products is black in colour. Specification articles (product selections) contained within square brackets [ ] are shown as example choices only.

Click Here to view Ecoglo Step Edge Products

| Product Code | Description |
| --- | --- |
| F15-175 Step Nosing | 75mm x 33mm aluminium (aluminum) nosing incorporating 12.6mm photoluminescent strip and 50mm black anti-slip strip. Available in lengths from 800mm to 1500mm in 100mm increments, or in full lengths of 2450mm or 3060mm. |
| F14-175 Step Nosing | 75mm x 10mm aluminium (aluminum) nosing incorporating 12.6mm photoluminescent strip and 50mm black anti-slip strip. Available in lengths from 800mm to 1500mm in 100mm increments, or in full lengths of 2450mm or 3060mm. |
| F15-173 Step Nosing | 75mm x 33mm aluminium (aluminum) nosing incorporating 25mm photoluminescent strip and 50mm black anti-slip strip. Available in lengths from 800mm to 1500mm in 100mm increments, or in full lengths of 2450mm or 3060mm. |
| F14-173 Step Nosing | 75mm x 10mm aluminium (aluminum) nosing incorporating 25mm photoluminescent strip and 50mm black anti-slip strip. Available in lengths from 800mm to 1500mm in 100mm increments, or in full lengths of 2450mm or 3060mm. |
| F2-003 Step Nosing | 77mm x 22mm aluminium (aluminum) nosing incorporating 26mm photoluminescent strip. Available in lengths from 800mm to 1500mm in 100mm increments, or in full lengths of 2450mm or 3060mm. |
| E2-071 Step Edge Contrast | 37mm wide strip incorporating 16mm photoluminescent strip and 21mm black anti-slip strip. Available in lengths from 800mm to 1500mm in 100mm increments, or in full lengths of 2450mm or 3060mm. |
| E14-075 Step Edge Contrast | 64mm wide strip incorporating 10mm photoluminescent strip and 50mm black anti-slip strip. Available in lengths from 800mm to 1500mm in 100mm increments, or in full lengths of 2450mm or 3060mm. |
| E15-073 Step Edge Contrast | 51mm wide strip incorporating 26mm photoluminescent strip and 25mm black anti-slip strip. Available in lengths from 800mm to 1500mm in 100mm increments, or in full lengths of 2450mm or 3060mm. |
| E4-073 Step Edge Contrast | 51mm wide strip incorporating 26mm photoluminescent strip and 25mm black anti-slip strip. Available in lengths from 800mm to 1500mm in 100mm increments, or in full lengths of 2450mm or 3060mm. |
| G6-003 Guidance Strip | 26mm wide photoluminescent strip suitable for step edging. Available in lengths from 800mm to 1500mm in 100mm increments, and in full length of 3060mm. |

B 	  Handrail Markings

1 			Handrail Markings Product Code: [H5-001]

Description: [27mm wide photoluminescent handrail strip
 			suitable for curved handrails. Available in 1000mm and 3060mm
 			lengths.]

SPEC NOTE: The listed italics data included in table below provide product codes and descriptions. Specification articles (product selections) contained within square brackets [ ] are shown as example choices only.

Click Here to view Ecoglo Handrail Products.

| Product Code | Description |
| --- | --- |
| H3-001 Handrail Strip | 15.5mm wide photoluminescent handrail strip suitable for curved handrails. Available in 1000mm and 3060mm lengths. |
| HREC3 End Cap | Metal End Cap for use with H3-001 |
| H5-001 Handrail Strip | 27mm wide photoluminescent handrail strip suitable for curved handrails. Available in 1000mm and 3060mm lengths. |
| HEC5 End Cap | Plastic End Cap for use with H5-001 |
| G3-001 Guidance Strip | 15.5mm wide photoluminescent strip suitable for flat handrails. Available in 1000mm and 3060mm lengths. |
| G6-003 Guidance Strip | 26mm wide photoluminescent strip suitable for flat handrails. Available in lengths from 800mm to 1500mm in 100mm increments, and in full length of 3060mm. |

C 	  Perimeter demarcation

1 	Perimeter Demarcation Product Code: [G3-001]

Description: [15.5mm wide photoluminescent strip. Available in
 			1000mm and 3060mm lengths.]

SPEC NOTE: The listed italics data included in table below provide product codes and descriptions. Specification articles (product selections) contained within square brackets [ ] are shown as example choices only.

Click Here to view Ecoglo Perimeter Demarcation Products.

| Product Code | Description |
| --- | --- |
| G3-001 Guidance Strip | 15.5mm wide photoluminescent strip. Available in 1000mm and 3060mm lengths. |
| G6-003 Guidance Strip | 26mm wide photoluminescent strip. Available in lengths from 800mm to 1500mm in 100mm increments, and in full length of 3060mm. |
| T6-101 Path Marker | 37mm wide aluminium extrusion incorporating 15.5mm wide photoluminescent strip. Available in 1000mm lengths. |
| T5-101 Path Marker | 51mm wide aluminium extrusions incorporating 15.5mm wide photoluminescent strip. Available in 1000mm lengths. |

D 	  Obstacle Marking

1 	Obstacle Marking Product Code: UL-HZ2503

Description: Manufactured from high quality vinyl tape.
 			Available in rolls 25mm wide x 3m. (Non-HTC Product)

Click Here to view Ecoglo Obstruction Marking Products.

E 	  Stairway Identification Signs

1 	Stairway Identification Signs Product Code: S5-SI4631

Description: Photoluminescent Floor Identification Signs. 18” by
 			12” (460mm x 310mm) with Tactile raised Floor level numbers
 			(ICC A117.1 compliant). Braille floor number optional. Signage
 			shall state the story of, and the direction to, the exit discharge
 			and the availability of roof access from the enclosure for the fire
 			department.

Click Here to view Ecoglo Stairway Identification Signs.

F 	  Photoluminescent Egress Signage

1 	Directional egress signage. 100 mm x 100 mm. Signs can be
 			used alone or in combination with other egress signage.

Click Here to view Ecoglo Egress Signage.

| Product Code | Description |
| --- | --- |
| S5-RML1010 | Directional pictogram – left facing. 100mm x 100mm.. |
| S5-RMR1010 | Directional pictogram – right facing. 100mm x 100mm |
| S5-ARS1010 | Directional arrow – straight. 100mm x 100mm |
| S5-ARD1010 | Directional arrow – diagonal. 100mm x 100mm |

G 	  Door Hardware Markings

1 	Door handle marker (100 mm x 100 mm).

2 	Door Push Bar Marker (407 mm x 38 mm). (Non-HTC product.)

Click Here to view Ecoglo Door Hardware Markings.

| Product Code | Description |
| --- | --- |
| S5-DHM1010 | Door handle marker. 100mm x 100mm |
| UL-DHM3840 | Door push bar marker with “PUSH TO OPEN” text on photoluminescent background. 407mm x 38mm. |

Part 3 Execution

3.1 	Examination

A 	  Before installation, examine surfaces on which the work of this section
 		  depends. Notify [Contractor] if substrates do not comply with
 		  requirements of this section

B 	  Ensure any painted surfaces are fully cured.

C 	  Do not proceed with work of this Section until all unsatisfactory
 		  conditions have been corrected, if any.

D 	  Commencement of Work will imply acceptance of surfaces.

3.2 	Preparation

A 	  Clean surfaces to remove dirt, dust, grease, oil, loose material, frost,
 		  paint, coatings, or other matter that may affect bonding or installation
 		  of photoluminescent products.

B 	  Test substrates for fit with products before using adhesives or
 		  mechanical 	fastening.

3.3 	Installation

A 	  Install signs [as per Schedule attached at end of Section] [as
 		  indicated in Drawings] [positioned in accordance with [National Fire
 		  Protection Association (NFPA) 101 - Life Safety Code] [International
 		  Building Code / International Fire Code (IBC/IFC)] [New York City
 		  RS6-1 and RS6-1A Photoluminescent Exit Path Markings]].

B 	  Unless otherwise indicated in the specifications, install Products in
 		  accordance with manufacturer’s instructions. Obtain written
 		  instructions directly from manufacturer.

3.4 	Cleaning

A 	  Trim any excess adhesive with a sharp blade.

B 	  At completion of installation, clean soiled Product surfaces in
 		  accordance with manufacturer’s instructions.

3.5 	Waste Management and Disposal

A 	  Separate waste materials for [reuse] [and] [recycling] at nearest used
 	      	  building materials facility.

B 	  Divert unused caulking, sealants and adhesive materials from landfill
 	      	  through appropriate disposal procedure listed in safety data sheets
 	      	  (SDS).

3.6 	Protection

A 	  Allow 24 hours for adhesive cure with no foot traffic permitted.

B 	  Protect areas from damage using barriers, markers or temporary
	      	  signs as required.

C 	  Do not allow heavy objects to come in contact with installed products.

End of Section